Supplemental Material for "Commissioning-Calibrated GP-HOCBF Safety Filtering for Ultra-Supercritical Boiler-Turbine Control under Model Mismatch"

Supplemental Material

Citation numbers follow the numbering of the main article.

1 Native-Sample Safety and QP Diagnostics

All benchmark violation rates are evaluated at the native 1 s controller instants. A controller sample is counted once when any enforced pressure, separator-enthalpy, or power barrier satisfies  in raw barrier units. The tolerance excludes numerical boundary roundoff; the unrounded minimum barrier is retained separately. Episode-level event probabilities are not combined with these sample rates.

Table S1. Count-level S3 diagnostics for the primary  validation. Each row aggregates 50 independent 500-sample rollouts. A rejected QP is non-converged, non-finite, or has maximum normalized primal residual above .

| Method | Violating samples | QP rejected | QP intervention |
| --- | --- | --- | --- |
| HOCBF, no GP | 9798 of 25,000 | 0 of 25,000 | 0.00% |
| RoCBF-SF tune-selected, | 0 of 25,000 | 0 of 25,000 | 41.32% |
| Full implemented-margin endpoint, | 9798 of 25,000 | 25,000 of 25,000 | 0.00% |

The tune-selected  row has no rejected QP in S3. The full implemented-margin row rejects every S3 QP, reverts to the upstream proposal, and consequently reproduces the no-GP violation count. This endpoint does not satisfy the robust-QP-feasibility assumption of Theorem 1.

2 Robustness-Factor Tune/Test Separation

Tune seeds 0–2 each contain 10 episodes of 500 controller samples. Thus, each  setting contains 15,000 tune samples. The predeclared selector is the smallest setting for which both pooled and maximum-per-seed violation rates are below 1% and both pooled and maximum-per-seed QP-rejection rates are below 0.5%.

Table S2. Tune-seed selection data. Rates are percentages of native controller samples. Wilson upper limits are descriptive Bernoulli-reference values; adjacent samples are serially correlated.

|  | Violation count (rate) | Max. seed violation | QP rejection count (rate) | Max. seed rejection | Pass |
| --- | --- | --- | --- | --- | --- |
| 0 | 0 (0.000) | 0.000 | 0 (0.000) | 0.000 | Yes |
| 0.01 | 0 (0.000) | 0.000 | 0 (0.000) | 0.000 | Yes |
| 0.02 | 0 (0.000) | 0.000 | 0 (0.000) | 0.000 | Yes |
| 0.05 | 0 (0.000) | 0.000 | 0 (0.000) | 0.000 | Yes |
| 0.10 | 0 (0.000) | 0.000 | 13 (0.087) | 0.120 | Yes |
| 0.20 | 4849 (32.327) | 37.540 | 11220 (74.800) | 87.660 | No |
| 0.50 | 5663 (37.753) | 40.140 | 14972 (99.813) | 99.880 | No |
| 1.00 | 5648 (37.653) | 40.000 | 15000 (100.000) | 100.000 | No |

The selector fixes  before evaluating seeds 3–4. Each held-out seed contains 25,000 samples. Both seeds record zero violating samples and zero rejected QPs, giving pooled counts of 0/50,000 for both diagnostics. The descriptive 95% Wilson upper reference for 0/15,000 tune-set violations is 0.0256%; serial correlation prevents interpreting this value as an independent-trial confidence bound. No holdout result is used to change , and zero observed events are not presented as zero event probability.

3 GP Residual Definition and Commissioning Data

The benchmark and deployed GP use the same three-dimensional kernel input,

|  | (S1) |
| --- | --- |

The nominal predictor uses the complete seven-state vector  and all three proposed control commands. The three learning targets are residual rates,

|  | (S2) |
| --- | --- |

Kernel distances use the frozen training transform , and each residual target is standardized by its training mean and standard deviation. The transforms are not updated online.

The plant commissioning record contains approximately 14 days of 1 Hz historian and commissioning data (about 1.21 million state transitions). Stops, manual operation, communication faults, stale measurements, interlock action, missing values, and identified bad points are removed, leaving approximately 250,000 candidate transitions. Days 1–10 form the training candidate pool; day 11 is a 24 h isolation gap; and days 12–14 form the independent validation pool. Normalization parameters and kernel hyperparameters use only days 1–10.

Table S3. Fixed plant-GP load strata and quotas. Candidates are separated by at least 60 s and selected by deterministic farthest-point coverage in standardized  space. Quotas are not borrowed between strata.

| Generator-load stratum (MW) | Training points | Validation points |
| --- | --- | --- |
| 180–264 | 100 | 40 |
| 264–363 | 100 | 40 |
| 363–462 | 100 | 40 |
| 462–561 | 100 | 40 |
| 561–660 | 100 | 40 |
| Total | 500 | 200 |

Three independent exact Matérn-5/2 GPs are trained and frozen after offline replay. The deployed dictionary remains at ; online sample growth is zero. Models are reviewed quarterly and after major maintenance or a material coal-source change. The current and previous stable versions are retained for rollback. Exact-GP storage is  and offline retraining is  for  outputs. Three float32 Cholesky factors occupy approximately 3 MB; training arrays, coefficients, and kernel parameters occupy approximately 10–20 MB. The deployed JAX process has a larger runtime resident set (approximately 0.5–2 GB), but this does not grow with online operation because the dictionary is frozen.

The controlled sensitivity experiment uses five independent seeds. Each of the nine dictionary-size–corruption settings therefore comprises five seeded fit-and-evaluation runs (45 runs in total). Each run fits three scalar-output GPs, one for each component of , giving 135 scalar GP fits. It then evaluates 200 held-out transitions and one 500-sample S3 closed-loop rollout. Corruption replaces 5% or 10% of selected training targets by signed three-training-standard-deviation offsets; it does not represent a measured plant bad-point rate.

Table S4. GP quantity/quality sensitivity. NRMSE and interval coverage are averaged over outputs and seeds. Closed-loop columns aggregate 2500 native controller samples per cell.

|  | Target corruption | Held-out NRMSE | 95% interval coverage | Violation, | QP rejection, | QP intervention |
| --- | --- | --- | --- | --- | --- | --- |
| 100 | 0% | 0.00090 | 100.00% | 0.00% | 0.00% | 41.80% |
| 250 | 0% | 0.00055 | 100.00% | 0.00% | 0.00% | 41.76% |
| 500 | 0% | 0.00046 | 100.00% | 0.00% | 0.00% | 41.76% |
| 100 | 5% | 0.54291 | 96.03% | 20.24% | 6.76% | 24.00% |
| 250 | 5% | 0.41965 | 97.13% | 5.76% | 4.04% | 37.12% |
| 500 | 5% | 0.06085 | 99.90% | 0.00% | 0.00% | 41.92% |
| 100 | 10% | 0.66568 | 96.37% | 15.12% | 8.60% | 27.16% |
| 250 | 10% | 0.44662 | 97.03% | 13.16% | 5.88% | 33.20% |
| 500 | 10% | 0.08745 | 99.80% | 0.00% | 0.00% | 41.32% |

The corrupted fits are deliberately evaluated without the pre-enable data-quality gate. The 100- and 250-point dictionaries show increased violations and QP rejection, while the 500-point dictionary retains zero observed violations and no rejection under both bounded fault-injection levels. The comparison therefore tests the joint effects of dictionary coverage and target quality; it does not imply that every corrupted fit fails or that the 500-point model is robust to arbitrary bad data. In deployment, held-out residual, coverage, and QP-feasibility checks are all required before a model receives write authority.

4 Coverage Monitoring and Fallback State Machine

The online input-coverage statistic and standardized innovation are

|  | (S3) |
| --- | --- |

Here , , , and  all have residual-rate units. Because the deployed sampling period is  s, this notation correction does not change the reported numerical thresholds.

Table S5. GP coverage and degradation thresholds used by the deployed supervisor.

| Monitor | Trigger | Action |
| --- | --- | --- |
| Input coverage | Any or outside the training 0.5th–99.5th percentile | Enter full-row nominal-HOCBF mode. |
| Posterior uncertainty | Above the validation-set 99th percentile | Withdraw GP mean correction. |
| Standardized innovation | Any for three cycles | Withdraw GP mean correction and alarm. |
| Severe innovation | Any once | Immediate live-DCS bypass. |
| Persistent OOD | More than 1% of cycles in one hour | Create an offline recalibration task. |
| Recovery | Ten consecutive cycles with valid input, innovation, and variance checks | Permit GP-mode recovery subject to controller authorization. |

Moderate coverage loss follows

|  | (S4) |
| --- | --- |

Invalid measurements or communication, non-finite/model-load faults, nominal-QP or actuator-constraint infeasibility, a direct physical-bound exceedance, pressure-low physical margin below 2.0 MPa, or a QP/task timeout bypasses the bounded degraded stage immediately. The nominal-HOCBF interval has no GP coverage claim.

An initially infeasible QP permits one reduced-QP retry only for the whitelisted pressure_low row. Let the physical command deviation be , with normalized , transformed row , and authority measure . Row removal requires

|  | (S5) |
| --- | --- |

with valid measurements and no active protection or interlock. The authority norm is evaluated after actuator normalization but before unit-row scaling. No actuator box/rate row or second CBF row can be removed, and only one retry is permitted. A successful reduced QP is reported as optimal_recovered; it is outside the full-row certificate.

The deployed task deadline is 1000 ms, equal to the controller period. The field QP timeout is 200 ms. A timeout, non-finite result, or failed retry returns the current live DCS command rather than the previous algorithm command. Three consecutive solve failures, communication loss beyond 3 s, a process restart, or a model-load fault latches bypass. Re-entry requires valid measurements, heartbeats, and dry-run QPs for ten cycles, DCS automatic mode, inactive protection/interlocks, operator reset acknowledgement, and the active Kubernetes lease. A 10 s linear blend is then used for bumpless transfer, provided the QP and DCS commands differ by no more than 2% of actuator range and both lie in the current feasible set.

Kubernetes uses a 3 s Lease renewed every 1 s. Only the lease holder may assert the local write permit; standby Pods connect to Modbus TCP read-only. The DCS remains the final write-permission owner and requires enable, automatic mode, no manual mode, valid echoed heartbeat with age no greater than 2 s, active lease ownership, and a fresh command sequence. Loss of any condition selects the live coordinated-control command.

5 Plant Historian and Controller-Export Evidence

The public production-evidence index separates historian context from controller execution. MW01–MW03 are post-retrofit low-to-mid-load historian windows used only to position measured load and main-steam pressure in the operating-envelope figure; they do not supply controller-internal QP fields. MW04–MW06 are confirmed two-hour plant-controller exports covering 480.7–629.7 MW. Each contains 1440 records at 5 s export spacing from a controller executing at 1 s, giving 4320 exported records rather than 4320 controller cycles. These exports directly support the timestamps, operating mode, QP/recovery status, logged margins, saturation flags, and timing statistics reported below. GP lifecycle, Kubernetes lease ownership, heartbeat/sequence checks, and DCS write-permission rules are deployment-configuration specifications; the exports do not expose every internal handshake transition.

The confirmed controller/historian mappings used in the revision are , , and . The independent tag DCS2_MAIN_PRESS is main-steam pressure. The exported PST_HI value is a main-steam-pressure replay bound, not the separator-pressure upper limit.

The cohort analysis uses 300 s historian records from 2024–2025 and 25 June–5 July 2026. Two-hour windows contain 24 consecutive records and advance every 30 min. All 24 load samples must lie in 195–700 MW; pressure, pressure setpoint, and fuel flow must be finite, pressure channels must lie in 5–35 MPa, and fuel flow must be positive. One-to-one matching without replacement minimizes a standardized sum of squared differences in mean load, 24-point load-profile RMSE, load range, and mean fuel/load ratio. The respective calipers are 10, 30, and 40 MW and 0.08. The complete derived pair table and hashes of the 24 monthly pre-retrofit query files and the post-retrofit query file are included in the reproducibility package.

Table S6. Recomputed load-matched historian cohort. Windows overlap because they advance every 30 min; the post-day cluster-bootstrap intervals are therefore descriptive and are not randomized-treatment confidence intervals.

| Quantity | Pre-retrofit | Post-retrofit | Difference or interval |
| --- | --- | --- | --- |
| Loaded candidate windows | 14,675 | 517 | 512 one-to-one pairs |
| Unique calendar days in pairs | 193 | 11 | – |
| Pressure-residual standard deviation, median (MPa) | 0.523 | 0.502 | 3.93% reduction |
| Absolute pressure-residual p95, median (MPa) | 1.082 | 1.085 | 0.30% increase |
| Pair fraction with lower standard deviation | – |  | 55.27% |
| Pair fraction with lower absolute-error p95 | – |  | 59.18% |
| Post-day cluster bootstrap, standard-deviation reduction | 10,000 resamples |  | 95% interval -13.0,14.7% |
| Post-day cluster bootstrap, p95 reduction | 10,000 resamples |  | 95% interval -9.4,13.1% |

Median pair-quality diagnostics are 1.32 MW mean-load difference, 15.37 MW load-profile RMSE, 5.24 MW load-range difference, and 0.0115 fuel/load difference. The broad cluster-bootstrap intervals show that the cohort supports operating-context consistency but not a precise population effect estimate. The native 5 s pair in the main article provides the higher-resolution response diagnostic; the controller exports separately establish online filter execution.

Table S7. High-load controller-export evidence. Direct margins are minima over all 1440 records in each window. “None” in the status column denotes no reduced-QP recovery and no saturation flag.

| Window | Load (MW) | Sep.-pressure low margin (MPa) | Main-pressure high margin (MPa) | Nearest enthalpy margin (kJ/kg) | QP/recovery record | QP/task p95 (ms) |
| --- | --- | --- | --- | --- | --- | --- |
| MW04 | 563.0–621.2 | 2.217 | 2.173 | 62.284 | 1397 optimal; 43 recovered; 1 fuel-sat. | 4.195 / 26.238 |
| MW05 | 547.9–629.7 | 3.438 | 1.483 | 20.354 | 1440 optimal; none | 4.074 / 26.139 |
| MW06 | 480.7–619.3 | 2.705 | 0.463 | 0.359 | 1440 optimal; none | 4.062 / 26.159 |

All 43 MW04 recovery records have FB_RSN=weak_authority_constraint_drop, ACT_CSTR=pressure_low, and negative MG_PLO. The diagnostic row ranges from -0.03266 to -0.00561, while the direct physical margin  ranges from 2.21654 to 2.36306 MPa and the other five exported HOCBF margins remain positive. MW05–MW06 contain no reduced-QP record. Across MW04–MW06, QP time has median/p95/maximum values 3.557/4.095/6.234 ms, and total task time has corresponding values 24.564/26.183/28.665 ms.

The plant value  is fixed after training-block replay and passes the one-pass time-isolated validation gate without retuning; it is not copied from the benchmark S3 selection. Record-level plant replay remains a restricted enterprise asset and is not inferred from the high-load controller exports. The original PID gains, output limits, anti-windup, sliding-pressure curve, coordinated-control logic, and fuel/feedwater/turbine-valve base loops are unchanged; RoCBF-SF is added downstream with enable, bypass, heartbeat, command-quality, and DCS-selection logic. The outage also includes instrument calibration, actuator inspection, combustion-equipment maintenance, and heat-surface cleaning, so the historian before/after comparison is observational. The controller exports separately establish that the proposed filter executed after restart.

The public reproducibility package contains source code, simulation results, derived historian metrics, bounded controller-export excerpts, field maps, and source/public hashes. Complete raw historian and original controller exports are enterprise assets. Qualified researchers may request restricted access from the corresponding author, subject to data-owner approval and the applicable data-use conditions.

6 Computation and Sampled-Data Boundary

The NMPC reference uses a warm-started SLSQP solve with horizon , output weights , input weights , normalized deviation-input bounds , six prediction constraints, additive disturbance correction with gain 0.5, maxiter=50, and ftol. Its convergence, residual, and computation-time statistics are regenerated with the actuator-augmented benchmark and reported from that frozen result set. These values describe the implemented reference rather than an optimized industrial MPC package.

Across the seven confirmatory conditions, pooled research-pipeline time per controller update ranges from 3.19 to 6.71 ms for the tune-selected RoCBF-SF row and from 3.75 to 20.82 ms for NMPC. NMPC records no solver failure and 0/175,000 observed state-limit violations in this implementation. These benchmark wall-clock measurements are distinct from the deployed-CPU evidence: the confirmed controller exports report a maximum QP time of 6.234 ms and a maximum total task time of 28.665 ms against the 1000 ms task deadline.

The theorem is continuous-time. The controller applies zero-order hold with  s because 1 s is the deployed coordinated-control task period; the safety filter therefore evaluates each upstream command update before the command-selection stage. This implementation choice does not assign a 1 s time constant to the slower boiler thermal dynamics. The field exports retain one record every 5 s, so their spacing is a logging interval rather than the internal control period. Field task timing establishes computational fit within the 1 s period but does not establish inter-sample forward invariance. Theorem 1 therefore is not presented as a sampled-data certificate; deriving such a certificate is retained as future work.

7 Proofs of Theoretical Results

7.1 Residual Cross-Term Bound

Lemma S1 (Residual cross-term bound).  Let  with . On the simultaneous residual event in Assumption 2 of the main article, suppose a valid pointwise derivative bound  is available on . Then

|  | (S6) |
| --- | --- |

Proof. By Cauchy–Schwarz,

|  | (S7) |
| --- | --- |

The simultaneous residual event gives  over the modeled outputs, which yields Eq. (S6). Smoothness on a compact operating set ensures that finite global derivative bounds exist when the required derivatives are bounded, but it does not identify them with . ◻

The online code uses  as a commissioning proxy for . Theorem 1 applies to that implementation only when Assumption 3 of the main article independently verifies that the resulting total margin dominates the true top-level HOCBF residual on .

7.2 Full Proof of Theorem 1

Proof of Theorem 1. Step 1 (Simultaneous residual event). Assumption 2 of the main article states that  holds simultaneously for the  modeled residual outputs and all  with probability at least . Condition on this event. The commissioning multiplier used in the numerical studies does not establish this event by itself.

Step 2 (Compositional bound). We show  by induction on .

- Base case (): . By Step 1 and triangle inequality, .

- Inductive step (): Assume . The residual recursion in the main article gives . The first term is bounded as in the base case. The second term is bounded by the induction hypothesis. Lemma S1 bounds the third term when a valid  is available. Assumption 3 requires the operator-norm and cross-term quantities used for the certificate to dominate these terms. Summing gives .

The implementation proxy is not substituted for  in this proof unless Assumption 3 validates that substitution.

Step 3 (Total perturbation). Combining the inductive bounds from Step 2 with the coupling-coefficient bound in Eq. (S8) yields  for every admissible deviation input . For , the applied margin is .

Step 4 (Forward invariance). For  satisfying , the definition  gives . Hence . Because , all lower-order recursive conditions in the main article’s definition of  are satisfied initially. The HOCBF forward-invariance theorem cited there therefore renders  forward invariant. ◻

7.3 Coupling Coefficient Gap Bound

The coupling coefficient gap is bounded by:

|  | (S8) |
| --- | --- |

where  and . This term is evaluated separately for each barrier row and included in that row’s total margin; Theorem 1 does not assume a fixed ratio between  and .